| Version | 6 | Developed by | Director of Property and Housing Services |
| --- | --- | --- | --- |
| Approval Date | 24/02/2026 | In Consultation With |  |
| Classification Type - (Confidential, Restricted, Internal use only, None) |  |  | Internal Use Only |

CONTENTS

- Introduction

- Purpose

- Responsibility

- Aims

5. 	Legislation

6.	Implementation

7. 	Competency

8. 	Monitoring

9. 	Review

Appendix 	Checklists

- Purpose and Scope

The electrical safety policy details how Framework meet the requirements for electrical safety under the Landlord and Tenant Act 1985, the Housing Act 2004, the Electricity at Work Regulations 1989 and the Electrical Equipment (Safety) Regulations 2016.  In addition to this, the policy provides assurance that measures are in place to ensure compliance with these regulations and to identify, manage and/or mitigate risks associated with electrical installations and electrical portable appliances.

The policy is relevant to all Framework employees, tenants, contractors and other persons who may work on, occupy, visit, or use its premises, or who may be affected by its activities or services.  It should be used by all to ensure they understand the obligations placed upon Framework to maintain a safe environment for tenants and employees within the home of each tenant and within all non-domestic (communal) premises or areas of buildings.

Framework will follow a systematic approach to the management of electrical work to ensure it meets the requirements set out in BS 7671 2018 Requirements for Electrical Installations IET Wiring Regulations 18th edition and other relevant legislation relating to electrical safety. This is to ensure the safety of tenants, employees and members of the public.

- Policy Statement

This policy demonstrates how Framework will comply with the above legislation for properties owned, leased and managed on behalf of others.

Framework will comply with the Electrical Safety Standards in the Private and Social Rented Sectors (England) Regulations 2020 as amended in 2025, ensuring five-yearly EICRs conducted by a qualified person. We will issue EICR copies to tenants within 28 days of inspection and before move-in for new tenancies, and we will complete remedial actions within 28 days (or sooner if specified by the report).”

It outlines our commitment to ensuring that we offer the best possible service to our tenants/residents in relation to electrical safety, it highlights our methods, targets and also makes tenants/residents and staff aware of their obligations in relation to electrical safety.

- Relevant Legislation and Guidelines

In the delivery of electrical safety Framework will ensure it meets the requirements of the Home Standard 2015. The standard applies to all registered providers. The Regulator of Social Housing’s role is to set the consumer standards and to intervene where failure to meet the standards has caused, or could have caused, serious harm to tenants.

- Safety and Quality Standard (Regulator of Social Housing) – consumer standard in force from 1 April 2024 covering stock condition, decency and health & safety outcomes.

- Electrical Safety Standards in the Private and Social Rented Sectors (England) Regulations 2020 as amended (2025 extension) – mandatory 5-year electrical installation checks for social as well as private rentals; phased dates for social housing apply: new tenancies from 1 Dec 2025; existing from 1 May 2026; all checks complete by 1 Nov 2026; remedial works within 28 days unless a shorter period is specified.

- BS 7671:2018 + A3:2024 (IET Wiring Regulations) – current national standard for design, installation and verification (note Amendment 4 scheduled for 15 Apr 2026).

- Electricity at Work Regulations 1989 (HSR25 guidance).

- IET Code of Practice for In-Service Inspection and Testing of Electrical Equipment (5th ed., 2020) and HSE INDG236/HSG107 – risk-based maintenance of portable/movable electrical equipment.

- Building Regulations 2010 – Approved Document P (2013) (electrical safety in dwellings).

- Regulatory Reform (Fire Safety) Order 2005 (as amended), Fire Safety Act 2021, and Fire Safety (England) Regulations 2022 (for blocks with common parts and high-rise duties).

- Smoke and Carbon Monoxide Alarm (Amendment) Regulations 2022 – duties on social landlords to fit and maintain alarms.

- Health and Safety at Work etc. Act 1974; MHSWR 1999; PUWER 1998; CDM 2015; Occupiers’ Liability Act 1984; RIDDOR 2013.

- UK GDPR and Data Protection Act 2018 (superseding the 1998 Act).

- Electrical Safety First Landlords’ Guide (2025)).

Framework will comply with HSE Codes of Practice and Guidelines, whilst not mandatory they are good practice and set out minimum expected levels and standards.

10. Awaab’s Law Compliance

Framework recognises the importance of Awaab’s Law in safeguarding tenants from serious health and safety hazards, including those related to electrical safety. In accordance with the Social Housing (Prescribed Requirements) (England) Regulations 2025, Framework will:

Awaab’s Law (from 27 October 2025) – phased scope and timeframes
Framework will comply with the Hazards in Social Housing (Prescribed Requirements) (England) Regulations 2025 (“Awaab’s Law”). From 27 Oct 2025 we will:

- Make safe all emergency hazards (any hazard posing an imminent and significant risk of harm) within 24 hours of becoming aware.

- Investigate significant damp and mould hazards within 10 working days, provide a written summary within 3 working days of investigation, and commence remedial works within 5 working days where a significant risk is identified (or within any shorter period specified by the Regulations/guidance).

- Maintain robust records of reports, inspections, decisions, communications and actions.
The Government will expand Awaab’s Law in 2026 to cover additional hazards (including fire and electrical hazards) presenting a significant risk of harm and broaden further in 2027 to most remaining HHSRS hazards. We will update this policy in line with these phases and may apply equivalent timeframes to electrical hazards ahead of Phase 2 as a proactive safety measure.

- Train staff to recognise and respond appropriately to electrical hazards and ensure that lifestyle assumptions are not used to dismiss tenant concerns.

Framework will continue to monitor regulatory updates as Awaab’s Law expands in 2026 and 2027 to cover additional hazards under the Housing Health and Safety Rating System (HHSRS), including fire and electrical risks. This policy will be updated accordingly to reflect future phases of the legislation.

- Responsibility

Framework acknowledges and accepts its responsibilities with regard to electrical safety under the Landlord and Tenant Act 1985, the Housing Act 2004, the Electricity at Work Regulations 1989 and the Electrical Equipment (Safety) Regulations 2016.

The Landlord and Tenant Act 1985 places duties on landlords to ensure that electrical installations in rented properties are:

- Safe when a tenancy begins

- Maintained in a safe condition throughout the tenancy

In order to be compliant under these duties electrical installations are required to be periodically inspected and tested.  The intervals between inspections are not absolutely set within any regulations, however, best practice guidance from the Electrical Safety Council and from BS7671: 2008 states that domestic electrical installations should be tested at intervals of no longer than 5 years from the previous inspection.

The responsibility for ensuring that electrical safety is carried out effectively is a key responsibility of the Property Services Manager

The operational responsibility for compliance and quality is the responsibility of the Repairs & Compliance Manager

The responsibility for ensuring that routine electrical repairs are undertaken promptly and safely is the responsibility of the Repairs & Compliance Manager.

Framework will undertake the following in relation to electrical safety in properties and communal areas:

- An Electrical Inspection Condition Report (EICR) on domestic and non-domestic (communal) properties every 5 years.

- Carry out electrical repairs as and when necessary.

- Quality checks of contractors undertaking work to electrical systems.

- An electrical safety check at a change of tenancy in accordance with legislative requirements and Framework procedures. See Section 4.7

- Test all Framework supplied electrical portable appliances periodically in accordance with the testing guidance set out in ‘The Code of Practice for In-Service Inspection and Testing of Electrical Equipment’ (ISITEE) and HSE leaflet INDG236(rev3).

- Carry out electrical installation inspection and tests and issue new satisfactory EICRs when completing planned component replacement works.

- Test and replace, as necessary, smoke alarms, heat detectors and carbon monoxide detectors.

Framework will not be responsible for:

- Tenants/Residents own electrical appliances.

Tenants/Residents have the following responsibilities:

- Ensuring that they use electrical services within Framework properties safely and responsibly. Tenants/ Residents should follow any advice given and ensure they do not operate or interfere with electrical installations in any way, which could endanger themselves or other building users.

- Allow access to their home so that we are able to undertake an electrical inspection of their property.

- Principles

Framework are committed to providing a robust, safe and cost-effective service to our customers in relation to electrical safety; In respect of electrical safety Framework will:

Hold accurate records against each property it owns or manages identifying when the electrical installation was last inspected and tested and all electrical portable appliances that is held at each property, together with details of all Portable Appliance Tests (PATs) undertaken.

Ensure that all domestic properties have a valid Electrical Installation Condition Report (EICR) that is no older than 5 years from the date of the previous EICR.  Framework will deliver a comprehensive program of testing and inspection of all domestic properties on a rolling 5-year cycle.

Ensure that all non-domestic (communal) properties and offices owned or managed have a valid Electrical Installation Condition Report (EICR) that is no older than 5 years from the date of the previous EICR. These frequencies may be varied subject to the following:

- The type and nature of the installation.

- Its use and operations.

- The quality and presence of maintenance regimes.

- External influences having a passive or active effect in the installation.

Framework will deliver a comprehensive program of testing and inspections of all non-domestic (communal) properties and offices on a rolling 5-year cycle.

Ensure that all electrical installations shall be in satisfactory condition following completion of an electrical installation inspection and test.

Make safe and/or where possible endeavour to repair all code 1 and code 2 defects identified by a periodic electrical installation inspection and test before leaving site after completing the inspection and testing works.  Any further remedial works to code 1 and 2 defects will be Actioned within 10 working days (except where a rewire is required) and an EICR will be issued stating that the installation is in a satisfactory condition following all completed remedial works.

Ensure that appropriate electrical installation inspection and tests or visual inspections are carried out prior to the commencement of any new occupancy (void properties), and that a satisfactory EICR is displayed at the property or placed within the hand over pack for the service user.

Framework will carry out either a visual check or an Electrical Installation Inspection and Test on empty properties.

Ensure that only suitably competent NICEIC electrical contractors and engineers undertake electrical works.

Ensure that all Framework electrical portable appliances are tested periodically in accordance with the testing guidance set out in ‘The Code of Practice for In-Service Inspection and Testing of Electrical Equipment’ (ISITEE).

Carry out electrical installation inspection and tests and issue new satisfactory EICRs when completing planned component replacement works within domestic properties.  In the case of a rewire Framework will receive an installation certificate and following minor works, a minor works certificate.

Test and replace as necessary smoke alarms, heat detectors and carbon monoxide detectors which are not covered as part of the annual gas safety check visit (i.e. the property does not have gas), as part of the 5-yearly electrical inspection and testing visit.

Ensure that robust processes and controls are in place to manage the completion of follow up works identified during inspection and testing of electrical installations and electrical portable appliances.

Ensure that robust processes and controls are in place to ensure that all electrical works are properly notified and approved under Part P of the Building Regulations for England and Wales, where this is required.

Ensure that robust processes and controls are in place to manage works to void and occupied properties that may affect existing electrical installations.

Have a robust process in place to gain access to properties where tenant/resident vulnerability issues are known or identified whilst ensuring timely access to any property in order to be compliant with this policy and safeguard the wellbeing of the tenant.

Engage with our tenants/residents in a participative and empowering manner so that they can contribute to the service provision with relation to electrical safety.

Fulfil our commitment to equality and diversity while delivering the electrical safety service to our tenants and residents.

Effectively maintain the housing stock and preserve its asset value.

Ensure that the electrical safety check is undertaken in compliance with relevant legislation, in a manner that promotes Value For Money.

6.    Implementation

To meet the aims of this policy, Framework will:

- Maintain all Framework-owned electrical systems in a safe condition and carry out Electrical Installation Condition Reports (EICRs) in accordance with current regulations.

- Ensure all electrical work is completed by competent and suitably qualified engineers

- Maintain clear procedures for completing electrical safety checks and repairs, including access arrangements and communication with tenants.

- Provide tenants with a copy of the EICR within 28 days upon request and retain records for at least 7 years.

- Maintain a property database detailing electrical safety history, appliance records, and access attempts.

- Ensure new-build properties are maintained by the developer during the warranty/defects period.

- Provide a 24/7 emergency service for electrical safety issues.

- Undertake EICRs or visual inspections on void properties prior to re-letting.

- Make electrical safety information available in accessible formats (e.g., large print, Braille, other languages).

- Ensure that tenants receive EICRs within 28 days of inspection or before move-in.

- Take legal action where access is repeatedly denied, in line with procedure.

7.    Competency

Framework will appoint a designated competent person, supported by a specialist Quality Assurance (QA) company, to oversee compliance with electrical safety legislation. This person will:

- Verify contractor competency and maintain records of qualifications.

- Ensure NICEIC (or equivalent) registration is current.

- Procure and review quality checks of contractor work.

- Confirm that contractors provide compliant risk assessments and health and safety documentation.

- Ensure Framework remains compliant with the Electricity at Work Regulations 1989 and the Electrical Equipment (Safety) Regulations 2016.

8.    Quality and Performance Monitoring

Framework is committed to maintaining high standards in electrical safety. To monitor performance and quality, we will:

- Conduct independent quality assurance checks on a representative sample of installations, repairs, and EICRs.

- Track and report performance indicators, including:
  - Properties requiring electrical safety checks
  - Percentage of properties with valid EICRs
  - Timeliness of remedial actions
  - PAT testing completion rates

- Survey tenant and resident satisfaction and use feedback to improve services.

- Provide opportunities for tenant/resident involvement in service monitoring.

- Effectively manage and monitor contractors delivering electrical safety and remedial works.

9.     Policy Review

Framework will review this strategy on a three yearly basis or as required following.

- New legislation.

- Emerging best practice.

- Day to day operational issues.

Sources (key evidence)

- Regulator of Social Housing — Safety and Quality Standard (effective 1 Apr 2024).

- Electrical Safety Regulations — Extension to Social Rented Sector (2025): GOV.UK guidance & legislation, CIH/NHF briefings (dates and remedials).

- Awaab’s Law — GOV.UK guidance and sector explainers (phasing, timescales, scope).

- BS 7671 updates — IET, Electrical Safety First, NICEIC; A3:2024 in force; A4 announced for Apr 2026.

- PAT/ITEE — HSE INDG236/HSG107 and IET Code of Practice (5th ed.).

- Smoke & CO alarms — 2022 amendments (social landlords in scope).

- Data protection — UK GDPR and DPA 2018 (replace DPA 1998).

- Electricity at Work Regulations 1989 (core H\&S duties).

More information on next pages below

Voids Procedure

Void Properties managed via the Housing Management Service (HMS) through Property Services with individual consumer units

As properties are vacated the Void Officer/responsible appointed person will run a system check to identify the date of issue of the current EICR, if the time period is within 12 calendar months of the issued date, they will instigate an internal visual electric check using the Framework generated inspection sheet. This will be saved alongside the valid EICR for information.  Any remedial works found not requiring any form of electrical certification to complete will be ordered and completed, if remedial works are found that require any form of electrical cert, we will request a new EICR and this will be saved to the system.

If a period of more than 12 months has elapsed, a full electrical inspection will be ordered and a new EICR will need to be generated. This will be saved on to the system generating a new renewal order date 60 months from the issued date.

Void Properties managed via HMS through Property Services within Shared houses containing communal consumer units

As a room becomes vacant the Void Officer/responsible appointed person will run a system check to identify the date of issue of the current EICR if this is within the 5 years renewal date they will instigate an internal visual electric check using the Framework generated inspection sheet. This on completion will be saved alongside the valid EICR for information.  Any remedial works found not requiring any form of electrical certification to complete will be ordered and completed, if remedial works are found that require any form of electrical cert, we will request a new EICR and this will be saved to the system.

Void Properties directly managed by scheme staff with either an Individual consumer unit or a communal consumer unit.

As properties/rooms are vacated the responsible appointed person will run a system check to identify the date of issue of the current EICR if this is within the 5 years renewal date they will instigate an internal visual electric check using the Framework generated inspection sheet.  This will be saved on to the system alongside the EICR. Any remedial works found will be ordered by the onsite team and completed following normal void repair ordering practices.

Appendix: Visual Electrical     Check Sheet

According to the Landlord and Tenant Act 1985, (England and Wales), section 11 places a duty on landlords to keep in repair and proper working order the Installations in the property for the supply of water gas and electricity and for sanitation.

In order to ensure compliance with the Electricity at Work Regulations 1989 and the continued electrical safety of your property and of your tenants, IET Guidance Note 3 on Inspection and Testing, (Table 3.2), recommends the maximum periods between inspection and testing at least every 5 years for privately rented dwellings. Then for non-rented domestic properties every 10 years. This test is called a periodic inspection and an Electrical Installation Condition Report (EICR) is produced.

However, for new or rewired properties, an Electrical Installation Certificate (EiC) should be accepted for installations under 5 years old in privately rented dwellings or 1O years in private dwellings. After which, an EICR should be undertaken, in line with the timescales outlined above.

When a Periodic Inspection is carried out and an EICR is issued, providing that all observation(s) coded, Cl, C2 and FI faults, (or action points), are addressed and rectified with supporting certificates of either an Electrical Installation Certificate, (EiC), or a Minor Electrical Installation Works Certificate, (MW), the electrical installation is classed as satisfactory.

The electrician who undertakes this EICR should be a skilled person registered with a Full Scope Electrical Competent Person Scheme who monitor and regularly assess the electrician, to prove their competency and to ensure that they have Public Liability insurance. It is then up to person contacting the electrician to ensure that they have Professional Indemnity insurance.

With an up to date EICR and with all action points cleared it is then recommended that a Routine Visual and Operational Check of the electrical installation is carried out every change of occupancy.

Guidance Note 3 section 3.5 informs us: that the routine check need not be carried out by an electrically skilled person but should be done by someone who is able to safely use the installation and recognise defects.

Supplementary to any electrical testing or to visual and operational checks, the landlord should instruct their tenants to report ASAP any breakages or excessive wear to the electrical installation or accessories so that repairs can be carried out. It should also be noted that the tenants are not to alter any electrical fittings without authorisation, as electrical testing and appropriate certificates are require.

| Pre Routine Visual and Operational Check list: Please ensure that the completed form is sent to property Services via email propertyservices@frameworkha.org this can either be a scanned or photograph copy. It is important that this document is completed and saved to ensure that Framework are compliant with electrical regulations. We may also be required to produce it in a court of law to help demonstrate that our duty of care has been met. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Full Property Address: Important that the full property address is entered here including the post code. |  |  |  |  |
| Property type | Circle appropriate |  |  | Action required |
| 1. a. Self-contained flat with its own consumer unit | Yes | No | N/A |  |
| b. Self-contained flat with shared communal consumer unit | Yes | No | N/A |  |
| c. Room with consumer unit | Yes | No | N/A |  |
| d. Room without consumer unit | Yes | No | N/A |  |
| e. Other: (note detail of provision) | Yes | No | N/A |  |
| 2. Property has an EICR, dated within the last 5 years | Yes | No | N/A |  |
| 3. All observation codes Cl, C2 and FI on the current EICR have been repaired and appropriate certification to verify this is held | Yes | No | N/A |  |
| 4. Date of last EICR | Date: |  |  |  |
| 5. Recommended date of next EICR (Normally 60 months from current cert) | Date: |  |  |  |
| Providing the answer to item 7a/b (as applicable) and 2 is yes and this Routine Visual and Operational Check is within the dates of item 3 and 4 then this check can commence, if not an EICR should be commissioned. |  |  |  |  |
| Checks to be Undertaken |  |  |  |  |
| 1. Electrical intake Position ( Meter/mains fuse/electrical tails) | Circle appropriate |  |  | Action required |
| a. The supplier’s fuse and meter seals are in place | Yes | No | N/A |  |
| b. Are there any visual signs of burning, overheating or damage or smell of burning at the electrical intake point (Meter/main fuse) | Yes | No | N/A |  |
| c. The electrical intake point is easily accessible and free from clutter | Yes | No | N/A |  |
| d. There are no signs of meter by pass to steal electricity | Yes | No | N/A |  |
| 2. Consumer unit (Fuse Box) | Circle appropriate |  |  | Action required |
| a. There is adequate space around the consumer unit with no combustible materials stored near | Yes | No | N/A |  |
| b. The consumer unit is correctly labelled for identification of circuits , RCD testing and date of next inspection | Yes | No | N/A |  |
| c. There are no blanks or lids missing from the consumer unit | Yes | No | N/A |  |
| d. All fuses and circuit breakers appear to be the same product type | Yes | No | N/A |  |
| e. Consumer unit appears in a visually satisfactory condition and free from dust, debris, damage and is securely mounted. | Yes | No | N/A |  |
| f. Functional check of consumer unit main switch and circuit breakers, switch on and off to make sure they are working | Yes | No | N/A |  |
| 3. Residual current device (rcd, rcbo, rccb) | Circle appropriate |  |  | Action required |
| a. 30mA RCD are present in the consumer unit or before the consumer unit | Yes | No | N/A |  |
| b. I have operated the test buttons on the RCDs during the course of this check and confirm they switch off | Yes | No | N/A |  |
| c. After consulting the staff/tenant, there is no regular tripping of either the RCD or circuit breakers to the best of my knowledge | Yes | No | N/A |  |
| 4. Main protective bonding | Circle appropriate |  |  | Action required |
| a. A bonding conductor is securely and correctly connected to the copper water pipe bonding clamp | Yes | No | N/A |  |
| b. A bonding conductor is securely and correctly connected to the copper gas/oil pipe bonding clamp | Yes | No | N/A |  |
| c. All bonding clamps are secure to gas or water pipes with BS951 label attached where accessible. | Yes | No | N/A |  |
| 5. Fixtures and fittings | Circle appropriate |  |  | Action required |
| All fittings (light fittings, sockets, switches, outlets, showers, storage heaters etc.) in the property are tightly fixed in to their back boxes with all screws present | Yes | No | N/A |  |
| b. All socket in the property are working; Advised to use a plugin socket tester | Yes | No | N/A |  |
| c. Are any of the fittings (light fittings, sockets, switches, outlets, showers, storage heaters etc.) in the property showing signs of burning or damage | Yes | No | N/A |  |
| d. There are no signs of uncertified modifications/alterations to the electrical installation by the tenant or others | Yes | No | N/A |  |
| 6. Electrical Appliances | Circle appropriate |  |  | Action required |
| a. All portable electrical appliances supplied by the landlord have been visually inspected as well as have a PAT test label showing it has past and is in date | Yes | No | N/A |  |
| 7. Additional checks smoke and carbon monoxide detectors | Circle appropriate |  |  | Action required |
| a. Smoke alarms /heat sensors fitted and all sound when test button pressed where appropriate | Yes | No | N/A |  |
| b. Carbon monoxide detectors where fitted, alarms sound if able to test | Yes | No | N/A |  |
| The above list is a guide only, the list is not exhaustive |  |  |  |  |
| Any action points, or issues that may warrant further inspection by a competent, registered electrical installer should be detailed here and raised with property services in the normal void repair ordering process. |  |  |  |  |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| This routine visual and operational check of the electrical installation is satisfactory, only if no action or remedial works are required | Satisfactory |  | Yes | No |
| I have carried out the above electrical checks on behalf of Framework Housing Association in line with the electrical safety policy |  |  |  |  |
| Job Title: Date: |  |  |  |  |
| Print Name: Signature: |  |  |  |  |

PAT Testing Timescales

| Equipment/Environment | User Checks | Formal Visual Inspection | Combined Inspection and Test |
| --- | --- | --- | --- |
| Battery-operated: (less than 40 volts) or Extra low voltage: (less than 50 volts AC): Telephone equipment etc. | No | No | No |
| Desktop computers, VDU screens | No | No | Yes - Every 3 Years |
| Photocopiers, Shredders, Printers, Scanners, Fridges, microwaves: Not hand-held. Rarely moved | No | No | Yes – Every 3 Years |
| Double insulated (Class II) equipment: Not hand-held. Moved occasionally, e.g. fans, table lamps | No | No | Yes – Every 3 Years |
| Double insulated (Class II) equipment: Hand-held, e.g. some floor cleaners, Hoovers. some kitchen equipment, food mixers. | Yes | No | Yes – Every 3 Years |
| Earthed equipment (Class I): Electric kettles, Toasters some floor cleaners, Hoovers, some kitchen equipment and irons | Yes | No | 1 Year |
| Cables and mains voltage extension leads and battery-charging equipment connected to the above rarely or occasionally moved equipment. | Yes | No | Yes – Every 3 Years |
| Cables and mains voltage extension leads and battery-charging equipment connected to frequently moved equipment. | Yes | no | 1 Year |
| Hand held construction electrical tools | Yes | No | 1 Year |